{"text_format":"2","workbook":"xls","n_sheets":2,"sheets":["Załacznik nr 1","Załacznik nr 2"],"not_rendered":{"charts":0,"images":2,"macros":0,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Załacznik nr 1","index":0,"n_rows":25,"n_cols":8,"rows_kept":25,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["Załącznik nr 1 do zadania 14"]
[]
["Budynek","Poziom","Strona","Nr pomieszczenia","Sterownik","TYP","Ilość modułów","OPIS"]
["Budynek A","Piwnica","Lewa","-002","1PL1","PRU 10.64",29,"Wymiana sterownika na nowy z Panelem lokalnym"]
["Budynek A","Piwnica","Prawa","-008","1PP7","PRU 10.64",26,"Wymiana sterownika na nowy z Panelem lokalnym"]
["Budynek A","Piwnica","Prawa","-008","1PP6","PRU 10.64",22,"Wymiana sterownika na nowy z Panelem lokalnym"]
["Budynek B","Piwnica","środek","-002","2PA5","PXC 64-U",19,"Dodatowy Panel"]
["Budynek C","Piwnica","Prawa","-007","2PA2","PRU 10.64",49,"Wymiana sterownika na nowy z Panelem lokalnym"]
["Budynek C","Piwnica","Lewa","-017","2PA1","PRU 10.64",42,"Wymiana sterownika na nowy z Panelem lokalnym"]
["Budynek C","Piętro 3","za łacznikiem","310/CD1","2PA4","PXC 64-U",15,"Dodatowy Panel"]
["Budynek C","Piętro 3","za łacznikiem","310/CD1","2PA3","PRU 10.64",38,"Wymiana sterownika na nowy z Panelem lokalnym"]
["Budynek A","Dach","Lewa","AD1","1PL3","PRU 10.64",34,"Wymiana sterownika na nowy z Panelem lokalnym"]
["Budynek A","Dach","Lewa","AD1","1PL4","PRU 10.64",18,"Wymiana sterownika na nowy z Panelem lokalnym"]
["Budynek A","Dach","Lewa","AD1","1PL1/W","pośrednia",8,"nie dotyczy"]
["Budynek A","Dach","Prawa","AD2","1PP9","PRU 10.64",37,"Wymiana sterownika na nowy z Panelem lokalnym"]
["Budynek A","Dach","Prawa","AD2","1PP8","PRU 10.64",38,"Wymiana sterownika na nowy z Panelem lokalnym"]
["Budynek A","Dach","Prawa","AD2","1PP67","pośrednia",23,"nie dotyczy"]
["Budynek B","Piwnica -2","Andiograf","Maszynownia","RW1","PXC100.D",16,"Zamontowany Panel PXM10"]
["Budynek B","Piwnica -2","Andiograf","Maszynownia","RW1","PXC200.D",21,"Zamontowany Panel PXM10"]
["Bydynek zew","Wytornica pary","Kontener","Kontener","-","-",4,"Moduły przygotowane do podpięcia do szyny komunikacyjnej sterownika 2PA1, przewódy komunikacyjne doprowadzone do szafy "]
["Zapasowy ","nie dotyczy","nie dotyczy","nie dotyczy","-","-","-","Sterownik nowy - zapasowy"]
[]
["Podsumowanie:"]
["Nowych sterowników - sztuk 11"]
["Paneli lokalnych  - sztuk 12"]

{"sheet":"Załacznik nr 2","index":1,"n_rows":18,"n_cols":5,"rows_kept":18,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["Załącznik nr 2 do zadania 14"]
[]
["LP.","Systemy Techniczne","Informacja o urzadzeniach/sterownikach","Komunikacja"]
["1.","Monitoring i zmiana parametrów Lodówek ","TELEMECANIQUE TWIDO TWLCA 40 DRF","Ethernet/MODNET"]
["2. ","Monitoring Kriostatów","TAYLOR-WHARTON, M505 CE-B + płytki komunikacyjne M309CE RS485","Nport/RS232","(lokalna magistrala po RS485)"]
["3.","Monitoring próżni","MIKSTER MCD-020 AVS_4 ","Nport/RS232"]
["4.","Monitoring TRAFO 1 i 2","MEDICON TSX Micro","Nport/RS232"]
["5.","Monitoring gazów Medycznych","MEDICON TSX Micro","Nport/RS232"]
["6.","Monitoring Ciekły Azot","MEDICON TSX Micro","Nport/RS232"]
["7.","Monitoring Węzeł pary (Poziom -2) Budynek C","Twido ","Nport/RS232"]
["8.","Monitoring wytwornicy pary ","Siemens Moduł 55,56,57,58","do podłączenia do magistrali sterownika simens 2PA1"]
["9.","Pomieszczenie Mroźni i Chłodni (Poziom -2)","RDC12 LEA Italy","Komunikacja ascii"]
["10.","Węzeł ciepła podstawowy i rezerwowy, Budynek A piwnica","TRAVIS 5479 SAMSON RS485","Nport/RS232"]
["11.","Bramka Grundfos","Grundfos G100 Gateway R/M/P V02","RS232"]
["12.","Monitoring agregatów na budynku B","Steronik Cariera","Nport/RS232"]
["13.","Czujniki ciśnienia od gazów medycznych ","MEDICON TSX Micro","Nport/RS232"]
["14.","Moritoring UPS","karta komunikacyjna UPS Galaxy 160","Nport/RS232"]
["15. ","Monitoring Energetyki ","MEDICON TSX Micro","Nport/RS232"]